## Sheet1
Combination Model | Component Units | Cooling Capacity (kW) | Capacity (HP) | Power Supply | Voltage Min (V) | Voltage Max (V) | Running Current (A) | Cooling Power Input (kW) | EER (kW/kW) | Starting Current | Weight (kg) | Colour | Compressor Type | Compressor Motor Output (kW) | Fan Unit Type | Fan Motor Output (kW) | Air Volume (m³/h) | Max External Static Pressure (P | Heat Exchanger Type | Refrigerant | Charge (kg) | High Pressure Switch | MCA (A) | MOCP (A) | Gas Pipe Diameter (mm) | Gas Conn. | Liquid Pipe Diameter (mm) | Liquid Conn. | Balance Pipe Diameter (mm) | Max No. of Connected Indoor Uni | Sound Pressure Level Cooling (d | Operation Temp Range Cooling (° | Notes
MMY-AP2617T8D-XA | MMY-MAP1407T8D-XA + MMY-MAP1207T8D-XA | 73.5 | 26 | 3N~50Hz 400V (380-415V) | 342 | 456 | 30.7 | 19.7 | 3.73 | Soft Start | 200+200 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 10.0×1 + 7.1×1 | Propeller fan | 1.0 + 1.0 | 12200 + 12200 | 40 | Finned tube | R410A | 6.0 + 6.0 | OFF:3.2 ON:4.15 | 50 | 64 | 34.9 | Brazing | 19.1 | Flare | 19.1 | 40 | 63.5 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP2817T8D-XA | MMY-MAP1407T8D-XA + MMY-MAP1407T8D-XA | 80 | 28 | 3N~50Hz 400V (380-415V) | 342 | 456 | 35.4 | 22.9 | 3.5 | Soft Start | 200+200 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 10.0×1 + 10.0×1 | Propeller fan | 1.0 + 1.0 | 12200 + 12200 | 40 | Finned tube | R410A | 6.0 + 6.0 | OFF:3.2 ON:4.15 | 52 | 64 | 34.9 | Brazing | 19.1 | Flare | 19.1 | 40 | 64 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP3017T8D-XA | MMY-MAP1607T8D-XA + MMY-MAP1407T8D-XA | 85 | 30 | 3N~50Hz 400V (380-415V) | 342 | 456 | 37.1 | 23.9 | 3.55 | Soft Start | 281+281 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 5.5×2 + 10.0×1 | Propeller fan | 1.0 + 1.0 | 12600 + 12200 | 40 | Finned tube | R410A | 8.0 + 6.0 | OFF:3.2 ON:4.15 | 55 | 64 | 34.9 | Brazing | 19.1 | Flare | 19.1 | 47 | 64 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP3217T8D-XA | MMY-MAP1607T8D-XA + MMY-MAP1607T8D-XA | 90 | 32 | 3N~50Hz 400V (380-415V) | 342 | 456 | 38.8 | 25 | 3.6 | Soft Start | 281+281 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 5.5×2 + 5.5×2 | Propeller fan | 1.0 + 1.0 | 12600 + 12600 | 40 | Finned tube | R410A | 8.0 + 8.0 | OFF:3.2 ON:4.15 | 58 | 64 | 34.9 | Brazing | 19.1 | Flare | 19.1 | 54 | 64 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP3417T8D-XA | MMY-MAP1807T8D-XA + MMY-MAP1607T8D-XA | 95.4 | 34 | 3N~50Hz 400V (380-415V) | 342 | 456 | 42.4 | 27.3 | 3.49 | Soft Start | 281+281 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 6.6×2 + 5.5×2 | Propeller fan | 1.0 + 1.0 | 12600 + 12600 | 40 | Finned tube | R410A | 8.0 + 8.0 | OFF:3.2 ON:4.15 | 64 | 66.5 | 34.9 | Brazing | 19.1 | Flare | 19.1 | 54 | 64.5 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP3617T8D-XA | MMY-MAP1807T8D-XA + MMY-MAP1807T8D-XA | 100.8 | 36 | 3N~50Hz 400V (380-415V) | 342 | 456 | 46 | 29.6 | 3.4 | Soft Start | 281+281 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 6.6×2 + 6.6×2 | Propeller fan | 1.0 + 1.0 | 12600 + 12600 | 40 | Finned tube | R410A | 8.0 + 8.0 | OFF:3.2 ON:4.15 | 66 | 65 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 62 | 65 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP3817T8D-XA | MMY-MAP2007T8D-XA + MMY-MAP1807T8D-XA | 106.4 | 38 | 3N~50Hz 400V (380-415V) | 342 | 456 | 50 | 32.1 | 3.31 | Soft Start | 281+281 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 7.8×2 + 6.6×2 | Propeller fan | 1.0 + 1.0 | 12600 + 12600 | 40 | Finned tube | R410A | 8.0 + 8.0 | OFF:3.2 ON:4.15 | 70 | 77 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 54 | 64.5 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP4017T8D-XA | MMY-MAP2007T8D-XA + MMY-MAP2007T8D-XA | 112 | 40 | 3N~50Hz 400V (380-415V) | 342 | 456 | 54 | 34.8 | 3.22 | Soft Start | 281+281 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 7.8×2 + 7.8×2 | Propeller fan | 1.0 + 1.0 | 12600 + 12600 | 40 | Finned tube | R410A | 8.0 + 8.0 | OFF:3.2 ON:4.15 | 77 | 84 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 65 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP4217T8D-XA | MMY-MAP1407T8D-XA + MMY-MAP1407T8D-XA + MMY-MAP1407T8D-XA | 120 | 42 | 3N~50Hz 400V (380-415V) | 342 | 456 | 53.1 | 34.3 | 3.5 | Soft Start | 200+200+200 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 10.0×1 + 10.0×1 + 10.0×1 | Propeller fan | 1.0 + 1.0 + 1.0 | 12200 + 12200 + 12200 | 40 | Finned tube | R410A | 6.0 + 6.0 + 6.0 | OFF:3.2 ON:4.15 | 78 | 81 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 66 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP4417T8D-XA | MMY-MAP1407T8D-XA + MMY-MAP1407T8D-XA + MMY-AP1607T8D-XA | 125 | 44 | 3N~50Hz 400V (380-415V) | 342 | 456 | 54.8 | 35.3 | 3.54 | Soft Start | 281+200+200 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 10.0×1 + 10.0×1 + 10.0×1 | Propeller fan | 1.0 + 1.0 + 1.0 | 12200 + 12200 + 12200 | 40 | Finned tube | R410A | 6.0 + 6.0 + 6.0 | OFF:3.2 ON:4.15 | 84 | 87 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 66.5 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP4617T8D-XA | MMY-MAP1807T8D-XA +MMY-MAP1407T8D-XA + MMY-MAP1407T8D-XA | 130.4 | 46 | 3N~50Hz 400V (380-415V) | 342 | 456 | 58.4 | 37.7 | 3.46 | Soft Start | 281+200+200 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 7.8×2 + 10.0×1 + 10.0×1 | Propeller fan | 1.0 + 1.0 + 1.0 | 12600 + 12200 + 12200 | 40 | Finned tube | R410A | 8.0 + 6.0 + 6.0 | OFF:3.2 ON:4.15 | 87 | 94 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 66 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP4817T8D-XA | MMY-MAP2007T8D-XA + MMY-MAP1407T8D-XA + MMY-MAP1407T8D-XA | 136 | 48 | 3N~50Hz 400V (380-415V) | 342 | 456 | 62.4 | 40.2 | 3.38 | Soft Start | 281+200+200 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 7.8×2 + 10.0×1 + 10.0×1 | Propeller fan | 1.0 + 1.0 + 1.0 | 12600 + 12200 + 12200 | 40 | Finned tube | R410A | 8.0 + 6.0 + 6.0 | OFF:3.2 ON:4.15 | 90 | 100 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 66.5 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP5017T8D-XA | MMY-MAP1407T8D-XA + MMY-MAP2007T8D-XA + MMY-AP1607T8D-XA | 141 | 50 | 3N~50Hz 400V (380-415V) | 342 | 456 | 64.1 | 41.2 | 3.42 | Soft Start | 281+281+200 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 10.0×1 + 10.0×1 + 10.0×1 | Propeller fan | 1.0 + 1.0 + 1.0 | 12200 + 12200 + 12200 | 40 | Finned tube | R410A | 6.0 + 6.0 + 6.0 | OFF:3.2 ON:4.15 | 94 | 97 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 66.5 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP5217T8D-XA | MMY-MAP2007T8D-XA + MMY-MAP1807T8D-XA + MMY-MAP1407T8D-XA | 146.4 | 52 | 3N~50Hz 400V (380-415V) | 342 | 456 | 67.7 | 43.6 | 3.36 | Soft Start | 281+281+200 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 10.3×2 + 5.5×2 + 10.0×1 | Propeller fan | 2.0 + 1.0 + 1.0 | 18500 + 12600 + 12200 | 40 | Finned tube | R410A | 10.0 + 8.0 + 6.0 | OFF:3.2 ON:4.15 | 96 | 103 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 67 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP5417T8D-XA | MMY-MAP2007T8D-XA + MMY-MAP2007T8D-XA + MMY-MAP1807T8D-XA | 152 | 54 | 3N~50Hz 400V (380-415V) | 342 | 456 | 71.7 | 46.2 | 3.29 | Soft Start | 281+281+200 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 6.6×2 + 7.8×2 + 6.6×2 | Propeller fan | 1.0 + 1.0 + 1.0 | 12600 + 12600 + 12600 | 40 | Finned tube | R410A | 8.0 + 8.0 + 8.0 | OFF:3.2 ON:4.15 | 100 | 104 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 67 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP5617T8D-XA | MMY-MAP2007T8D-XA + MMY-MAP2007T8D-XA + MMY-AP1607T8D-XA | 157 | 56 | 3N~50Hz 400V (380-415V) | 342 | 456 | 73.4 | 47.1 | 3.33 | Soft Start | 281+281+281 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 7.8×2 + 7.8×2 + 5.5×2 | Propeller fan | 1.0 + 1.0 + 1.0 | 12600 + 12600 + 12600 | 40 | Finned tube | R410A | 8.0 + 8.0 + 8.0 | OFF:3.2 ON:4.15 | 113 | 132 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 66.5 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP5817T8D-XA | MMY-MAP2007T8D-XA + MMY-MAP2007T8D-XA + MMY-AP1807T8D-XA | 162.4 | 58 | 3N~50Hz 400V (380-415V) | 342 | 456 | 77 | 49.5 | 3.28 | Soft Start | 281+281+281 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 7.8×2 + 7.8×2 + 6.6×2 | Propeller fan | 1.0 + 1.0 + 1.0 | 12600 + 12600 + 12600 | 40 | Finned tube | R410A | 8.0 + 8.0 + 8.0 | OFF:3.2 ON:4.15 | 119 | 140 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 67 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)
MMY-AP6017T8D-XA | MMY-MAP2007T8D-XA + MMY-MAP2007T8D-XA + MMY-AP2007T8D-XA | 168 | 60 | 3N~50Hz 400V (380-415V) | 342 | 456 | 81 | 52.2 | 3.22 | Soft Start | 281+281+281 | Silky shade (Munsell 1Y8.5/0.5) | Hermetic twin rotary | 7.8×2 + 7.8×2 + 7.8×2 | Propeller fan | 1.0 + 1.0 + 1.0 | 12600 + 12600 + 12600 | 40 | Finned tube | R410A | 8.0 + 8.0 + 8.0 | OFF:3.2 ON:4.15 | 126 | 150 | 41.3 | Brazing | 22.2 | Flare | 22.2 | 64 | 67 | -5.0 to 52.0 | (*1)(*2)(*3)(*4)(*5)