## Sheet1
MODEL NAME | Power supply | Cooling capacity (KW) | Heating capacity (KW) | Running current | Power consumption | Starting current | FCU dimension HEIGHT(MM) | FCU dimension WIDTH(MM) | FCU dimension DEPTH(MM) | Total weight | Heat exchangere | Soundproof / Heat-insulation material | Fan | Air flow volume (m^3/h) | Sound pressure (dB(A)) | Motor output (W) | Conecting pipe Gas side (MM) | Conecting pipe liquid side (MM) | Conecting pipe Drain side (MM) | Operating Range COOLING | Operating Range HEATING
UP0091HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 2.8 | 3.2 | 0.23 | 0.021 | 0.3 | 256 (30) | 840 (950) | 840 (950) | 18 (4) | Finned tube | Non-flammable insulation | Turbo fan | 800 / 730 / 680 | 30 / 29 / 27 | 14 | Ø9.52 | Ø6.35 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46
UP0121HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 3.6 | 4 | 0.23 | 0.021 | 0.3 | 256 (30) | 840 (950) | 840 (950) | 18 (4) | Finned tube | Non-flammable insulation | Turbo fan | 800 / 730 / 680 | 30 / 29 / 27 | 14 | Ø9.52 | Ø6.35 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46
UP0151HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 4.5 | 5 | 0.27 | 0.023 | 0.33 | 256 (30) | 840 (950) | 840 (950) | 20 (4) | Finned tube | Non-flammable insulation | Turbo fan | 930 / 830 / 790 | 31 / 29 / 27 | 14 | Ø12.7 | Ø6.35 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46
UP0181HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 5.6 | 6.3 | 0.29 | 0.026 | 0.36 | 256 (30) | 840 (950) | 840 (950) | 20 (4) | Finned tube | Non-flammable insulation | Turbo fan | 1050 / 920 / 800 | 32 / 29 / 27 | 14 | Ø12.7 | Ø6.35 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46
UP0241HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 7.1 | 8 | 0.38 | 0.036 | 0.42 | 256 (30) | 840 (950) | 840 (950) | 20 (4) | Finned tube | Non-flammable insulation | Turbo fan | 1290 / 920 / 800 | 35 / 31 / 28 | 20 | Ø15.9 | Ø9.52 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46
UP0271HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 8 | 9 | 0.38 | 0.036 | 0.42 | 256 (30) | 840 (950) | 840 (950) | 20 (4) | Finned tube | Non-flammable insulation | Turbo fan | 1290 / 920 / 800 | 35 / 31 / 28 | 20 | Ø15.9 | Ø9.52 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46
UP0301HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 9 | 10 | 0.43 | 0.043 | 0.59 | 256 (30) | 840 (950) | 840 (950) | 20 (4) | Finned tube | Non-flammable insulation | Turbo fan | 1320 / 1110 / 850 | 38 / 33 / 30 | 20 | Ø15.9 | Ø9.52 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46
UP0361HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 11.2 | 12.5 | 0.73 | 0.088 | 0.87 | 319 (30) | 840 (950) | 840 (950) | 25 (4) | Finned tube | Non-flammable insulation | Turbo fan | 1970/1430/1070 | 43 / 38 / 32 | 68 | Ø15.9 | Ø9.52 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46
UP0481HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 14 | 16 | 0.88 | 0.112 | 1.23 | 319 (30) | 840 (950) | 840 (950) | 25 (4) | Finned tube | Non-flammable insulation | Turbo fan | 2130/1430/1130 | 46 / 38 / 33 | 72 | Ø15.9 | Ø9.52 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46
UP0561HP-E | 1 ph 50Hz 220-240V , 1ph 60Hz 208-230V | 16 | 18 | 0.88 | 0.112 | 1.26 | 319 (30) | 840 (950) | 840 (950) | 25 (4) | Finned tube | Non-flammable insulation | Turbo fan | 2130/1520/1230 | 46 / 40 / 33 | 72 | Ø15.9 | Ø9.52 | 25 (Polyvinyl chloride tube) | 5 ~ 46 - 52 (*2) | -10 ~ 46